# Section 23 84 16

# DriSteem, Dehumidification System, RL Series

### PART 1 — GENERAL

#### 1.1	Summary

##### Section includes:

###### DRI-STEEM Corporation, dehumidifiers, RL series

#### 1.2	References

##### Certifications:

###### ETL, 60335-2-40

#### 1.3	Submittals

##### Comply with Submittal Procedures and Execution and Closeout Requirements in General Requirements.

##### Submit product data (manufacturer’s specifications, and technical data including performance, construction and fabrication) for each manufactured component.

#### 1.4	Warranty

##### Product shall be warranted to be free from defects in materials and fabrication for a period of two years after installation or 27 months from ship date with 36 months extended warranty automatically included for all DriSteem Dehumidifiers.

### PART 2 — PRODUCTS

#### 2.1	Dehumidifier shall be DRI-STEEM RL Dehumidification System or engineer-approved equal.

##### Fabrication requirements:

          - RL enclosure shall be constructed with 20-gauge painted galvannealed steel cabinet, polyester powder coat finish.

          - Enclosure shall have separate compartments: one for refrigeration components and one for electrical components. Enclosure shall be designed and secured to prevent accidental contact with electrical components. The front or top exterior of the cabinet shall contain the controller’s touch keypad.

###### The dehumidifier enclosure shall have pre-punched mounting holes for ease hanging, floor mounting and leveling.

###### Drain: PVC tubing.

#### 2.2	FAN/MOTOR

##### Unit shall include a single inlet centrifugal impeller (backward curved).

Material shall be molded polymer.

##### Motor shall include integral electronically commutated external rotor motor with integral controller (RL-9, RL-14, RL-31) or PSC motor (RL-3, RL-4, RL-6).

#### 2.3	FILTERS

##### Filter Section: Pleated, disposable pre-filters in supply-air. Filter shall be 2 inches (50 mm) thick (RL-9,RL-14, RL-31), 1 inches (25 mm) thick (RL-3, RL-4, RL-6) easily replaceable, with a minimum efficiency report value (MERV) of 11.

#### 2.4	COOLING

##### Refrigeration Package: Comply with UL 60335-2-40: Particular Requirements for Electrical Heat Pumps, Air-Conditioners and Dehumidifiers (RL-9, RL-14, RL-31) or UL 1995: Standard for Safety, Heating and Cooling Equipment.

Refrigerant Coils: Copper tubes with mechanically bonded aluminum fins (RL-9, RL-14, RL-31) or aluminum tubes with mechanically bonded aluminum fins (RL-3, RL-4, RL-6); factory fabricated and tested; multiple evaporator & condenser circuits, copper headers with brazed connections, and aluminum frame. Coils shall have a 800-psig (5516-kPa) pressure rating and be factory tested to 450 psig (3103 kPa).

Compressors: Hermetic, rotary compressor with integral vibration isolators with thermal-expansion valves (RL-9, RL-14, RL-31), capillary tubes (RL-3, RL-4, RL-6), filter-dryers (RL-9), accumulator.

Refrigerant:  R-410A

Capacity Control: Cycled compressor.

##### Safety Devices:

Compressor Motor Overload Protection:

System current limit of 20.96-A. The control algorithm will reduce the compressor speed by 2 Hz when measured current exceeds 20.96-A (RL-31).

Thermal Overload Switch integral to compressor (RL-3, RL-4, RL-6, RL-9, RL-14).

High temperature sensor protection: high temperature thermistor cuts off the compressor when the discharge temperature reaches 190°F (88°C).

Compressor drive-board built-in current, voltage, and temperature protection (RL-31).

Antirecycling Timing Device:  Prevent compressor restart for three minutes after shutdown.

#### 2.5	Electrical

##### Corded device with 10 foot (3 meter) cord (RL-9, RL-14, RL-31) and 8 foot (2.43 meter) 			cord (RL-3, RL-4, RL-6).

##### Removable cord for hard-wiring application (RL-9, RL-14, RL-31).

#### 2.6	RL Dehumidifier Controls

##### Adjustable set point control of dehumidifier.

##### Microprocessor controller with the following features or functions:

Keypad/display operable within a temperature range of 32 to 158 (F (0 to 70 (C), and that provides backlighting for viewing in low light.

Alarms, unit configuration values shall remain in nonvolatile memory indefinitely during a power outage.

The capability to monitor, control, and/or adjust the following parameters:

- Relative humidity (RH) set point, space temperature.

- System alarms and system messages

- Outputs for remote signaling of alarms, or for

- System diagnostics that include:

                - Test outputs function to verify component operation.

                - Test dehumidifier function, by simulating demand to validate performance.

#### 2.7	RL Dehumidifier Control Options

##### Control input accessory options:

Humidistat, electronic, BACnet, room: Electronic humidistat MSTP protocol, with internal sensor and touchscreen digital display showing both current humidity and humidity setpoint shall be wall-mounted. Accuracy to be +/-3% or better in operating range (0 to 90% RH and 32 to 122 °F [0 to 50°C]). 24 VAC/VDC power input required.

Humidistat, electronic, BACnet, duct: Electronic humidistat MSTP protocol, 2-piece kit includes digital wall controller showing both current humidity and humidity setpoint, and duct sensor that shall be installed in the duct. Accuracy to be +/-3% or better in operating range (0 to 90% RH and 32 to 122 °F [0 to 50°C]). 24 VAC/VDC power input required.

Humidistat, D77 controller, room: Control range 35-80%, accuracy of +- 5%, deferential 3%RH Low limit 40°F (4.4°C) due point and high limit is 99°F (37°C) dry bulb. Complete error code reporting

Alert light wire harness will illuminate when error occurs.

User-settable demand signal via normally open dry contact.

#### 2.8 	Dehumidifier Accessories

##### Leveling feet: Attached for RL-3, RL-4, RL-6, RL-9. Optional for RL-14 and RL-31.

##### Adjustable foot kit to facilitate floor mounting of dehumidifier.

Adjustable height for drain clearance and to ensure unit remains level.

##### Duct kit: Included (RL-3, RL-4, RL-6). Optional for RL-9, RL-14 and RL-31.

##### Duct collar kit to transition to a round duct for connection to an airstream.

Transition to include provision means for easy filter removal and replacement.

Static pressure not to exceed 0.6” w.c. (149 Pa).

### PART 3 — EXECUTION

#### 3.1	Installation

##### Install per manufacturer's printed instructions and as indicated on drawings.

##### Coordinate electrical connections specified in Division 23.

END OF SECTION