SECTION 23 84 13

Ultra-sorb® Models LV and LH Steam Dispersion Panel Humidifiers
 seq article \h\r0 PART 1 – GENERAL

1.1
Summary
A. Section includes:

1. DRI-STEEM Corporation, Ultra-sorb steam dispersion panels
1.2
References
A. Certifications

1. OSHPD Special Seismic Pre-approval

2. IBC 2009 Seismic Qualification
1.3
Submittals 
A. Comply with Submittal Procedures and Execution and Closeout Requirements in General Requirements. 

B. Submit product data (manufacturer’s specifications and technical data including performance, construction, and fabrication) for each manufactured component.

1.4
Warranty
A. Product shall be warranted to be free from defects in materials and fabrication for a period of two years after installation or 27 months from ship date.

 seq article \h\r0 PART 2 – PRODUCTS

2.1
Humidifier shall be DRI-STEEM Ultra-sorb Steam Dispersion Panel or engineer-approved equal.
A. The Ultra-sorb Models LV and LH steam dispersion panel shall directly inject pressurized boiler steam or evaporative, non-pressurized steam into ducted air for humidification.

B. Steam, dispersion panels shall be factory-assembled and include the following components:

1. Steam supply header/separator

2. Condensate collection header

3. Closely-spaced steam dispersion tubes spanning the distance between the two headers

C. Each dispersion tube shall be fitted with two rows of steam discharge tubelets inserted into the tube wall, centered on the diametric line, and spaced 1.5" (38 mm) apart. Each tubelet shall be made of a thermal-resin material designed for high steam temperatures. The two rows of tubelets in each dispersion tube shall discharge steam in diametrically opposite directions, perpendicular to airflow.
D. Each tubelet shall extend through the wall of and into the center of the dispersion tube and contain a steam orifice sized for its required steam capacity.
E. The humidifier shall provide absorption characteristics that preclude water accumulation on any in-duct surface within _____" (_____ mm) of the humidifier tube panel while maintaining conditions of _____% maximum relative humidity (RH) at a minimum of ​​​​_____(F (_____(C) in the duct airstream.

F. Air pressure loss across the humidifier panel shall not exceed _____" water column (_____ Pa) at a duct air velocity of _____fpm (_____m/s).
G. Each packaged humidifier panel assembly of tubes and headers shall be contained within a galvanized metal casing to allow convenient duct mounting, or to facilitate the stacking of and/or the end-to-end mounting of multiple humidifier panels in ducts or air handler casings. When so designated, the humidifier panel shall be shipped unassembled.
H. All tubes and headers shall be 304 stainless steel, and welded joints shall be Heli-arc welded.
I. Tubes shall be joined to headers with slip-fit couplings to facilitate easy removal.
J. Steam trap(s): 

1. Humidifier shall have one float and thermostatic (F&T) traps.

2.2
Humidifier Options
A. Optional stainless steel components:
1. Inlet strainer shall be stainless steel.

2. Entire valve shall be stainless steel.

3. Tubes and headers shall be 316 stainless steel and be Heli-arc welded.
4. Casing assembly shall be 304 stainless steel.

5. Headers shall be 316 stainless steel and be Heli-arc welded.

B. Valve options:

1. Modulating electronic humidification steam control valve: Valve shall be a normally closed with an electronic actuator. Valve trim shall be stainless steel and sized to meet humidification requirements. Actuator shall respond to a variable electronic signal. Available signal inputs: 4 to 20 mA, 2 to 10 VDC.

C. High-efficiency dispersion tube option:

1. Dispersion tubes shall be insulated with a plenum-approved insulating material for in-duct installation and have an R-value not less than 0.5 at a thickness not more than 0.125" (3.2 mm), for minimal increase in dispersion tube diameter.

2. Airstream heat gain shall not exceed the values as scheduled; the values shall be supported by the manufacturer's published data.

3. Insulating material shall meet the following criteria at 0.125" (3.2 mm) thickness:

a. Fire/smoke index shall be 0/0 per any of the following test procedures:
-  UL 723 fire/smoke index (Test for Surface Burning Characteristics of Building Materials) 
-  NFPA 255 (Standard Method of Test of Surface Burning Characteristics of Building Materials)
-  ASTM E84 (Surface Burning Characteristics for Materials Used in Plenums)
b. Stable up to 300 °F (148 °C) continuous — to prevent material degradation, hardening, or crumbling at high temperatures

c. Closed-cell construction does not absorb water or support microbial growth — to negate the need for vapor barriers and jackets

d. Non-toxic and pure as documented in manufacturer's data — to prevent off-gassing and to facilitate use in clean rooms, pharmaceutical applications, and food industries

e. Will not degrade when exposed to UVC light — to negate the need for UV wraps

f. Continuous, seam-welded, and held in place without bands or clamps — to minimize surfaces for the accumulation of particulate matter
D. Humidifier shall meet OSHPD Special Seismic Pre-approval for a SDS = 2.0 g for AHU applications and SDS = 2.5 g for duct applications.
E. Humidifier shall meet IBC 2009 Seismic Qualification by shake table testing for a SDS = 2.0 g for AHU applications and SDS = 2.5 g for duct applications.
2.3
Humidifier Control Options
A. Control input accessory options:

1. Humidistat, electronic, room:  Electronic humidistat with internal sensor and modulating output (0-10 VDC or 4-20 mA) and digital display showing both current humidity and humidity setpoint shall be wall-mounted. Accuracy to be +/-3% or better in operating range (0 to 90% RH and 32 to 122 F). 24 VAC/VDC power input required.
2. Humidistat, electronic, duct: Electronic humidistat, 2-piece kit includes digital wall controller showing both current humidity and humidity setpoint, and duct sensor that shall be installed in the duct.  It has modulating output 0-10 VDC or 4-20 mA. Accuracy to be +/-3% or better in operating range (0 to 90% RH and 32 to 122 F). 24 VAC/VDC power input required.
3. Humidistat, electronic, BACnet, room: Electronic humidistat, includes BACnet MSTP interoperability protocol, with internal sensor and modulating output (0-10 VDC or 4-20 mA) and touchscreen digital display showing both current humidity and humidity setpoint shall be wall-mounted. Accuracy to be +/-3% or better in operating range (0 to 90% RH and 32 to 122 F). 24 VAC/VDC power input required.
4. Humidistat, electronic, BACnet duct: Electronic humidistat, includes BACnet MSTP and BACnet IP interoperability protocol, 2-piece kit includes digital wall controller showing both current humidity and humidity setpoint, and duct sensor that shall be installed in the duct. It has modulating output 0-10 VDC or 4-20 mA. Accuracy to be +/-3% or better in operating range (0 to 90% RH and 32 to 122 F). 24 VAC/VDC power input required.
5. Airflow proving switch, pressure type: Airflow proving switch shall be diaphragm-operated with pitot tube for field installation. Switch shall have an adjustable control point range of 0.05" to 12" wc 
(12.5 to 2988 Pa). Operating temperature range -40 to 180 (F (-40 to 82 (C). Compatible with 24, 120, and 240 VAC.

6. Airflow proving switch, sail type: Airflow proving switch shall be a sail-operated electric switch for field installation. Switch makes at 250 fpm (1.3 m/s), and breaks at 75 fpm (0.4 m/s). Maximum operating temperature for sail: 170 (F (77 (C). Maximum operating temperature for switch: 125 (F (52 (C).
2.4
Humidifier Accessories

A. Pump, low-flow, high-temperature: Pump shall be suitable for pumping water up to 212 °F (100 °C). Maximum pump flow rate shall be 3.8gpm (228 gph) with a 12-foot head (36 kPa). Pump shall have a 1-gallon cast aluminum reservoir with a 3/8" pipe thread (DN10) outlet connection, two 1-1/4" (DN32) inlet openings, and integral float switch. Pump shall be used with 115 VAC. Pump also available with 230 VAC. Pump shall be UL recognized and wired per NEC requirements. Pump shall be equipped with low voltage auxiliary switch.

B. Pump, high-flow, high-temperature: Pump shall be suitable for pumping water up to 212 °F (100 °C). Maximum pump flow rate shall be 55 gpm (3300 gph) with a 12-foot head (36 kPa). Pump shall have a 4-gallon cast aluminum reservoir with vapor seal, a 3/4" pipe thread (DN20) outlet connection, a 1-1/2" pipe thread (DN40) inlet connection, and integral float switch. Pump shall be used with 115 VAC. Pump can be wired for use with 115/230 VAC. Pump shall be UL recognized and wired per NEC requirements. Pump shall be equipped with low voltage auxiliary switch.

C. Pump, high-flow, low-temperature: Pump shall be suitable for pumping water up to 150 (F (65.5 °C). Maximum pump flow rate shall be 55 gpm (3300 gph) with a 12-foot head (36 kPa). Pump shall have a 2-gallon cast aluminum reservoir, a 1" pipe thread (DN25) outlet connection, a 1-1/2" pipe thread (DN40) inlet connection, and integral float switch. Pump shall be used with 115 VAC. Pump can be wired for use with 115/230 VAC. Pump shall be UL recognized and wired per NEC requirements. Pump shall be equipped with low voltage auxiliary switch.

D. Drane-kooler™ water tempering device. A thermostatically controlled water valve shall meter an amount of cold water into a stainless steel mixing chamber to temper 212 (F (100 (C) water with a 6 gpm (0.38 L/s) in-flow rate to a 140 (F (60 (C) discharge temperature to sanitary system.

 seq article \h\r0 PART 3 – EXECUTION

3.1
Installation

A. Install per manufacturer's printed instructions and as indicated on drawings.

B. Coordinate electrical connections specified in Division 26.

END OF SECTION
DRI-STEEM® Guide Specification
Section 23 84 13

January 27, 2026
Page 1 of 3 
Ultra-sorb® Models LV and LH Steam Dispersion Panel

