- SECTION 23 25 00

- Deionized (DI) Systems

### PART 1 — GENERAL

#### 1.1	Summary

##### Section includes:

###### DriSteem deionized systems, which includes:

System controls

System options

##### Related items:

###### Electrical Service and Connections: Division 26

#### 1.2	References

##### Quality assurance:

###### ISO 9001-2015 certified

#### 1.3	Submittals

##### Comply with Submittal Procedures and Execution and Closeout Requirements in General Requirements.

##### Submit product data (manufacturer’s specifications and technical data including performance, construction and fabrication) for each manufactured component.

#### 1.4	Warranty

##### Product shall be warranted to be free from defects in materials and fabrication for a period of two years after installation or 27 months from ship date.

### PART 2 — PRODUCTS

#### 2.1	System shall be DriSteem DI systems or engineer-approved equal.

##### Fabrication requirements

###### Filter housing, two in series, construction

Polypropylene body and cap

EPDM o-ring

Initial pressure drop of housing no greater than 2 psig (13.8 kPa) at 15 gpm (0.95 l/s)

###### Filter Cartridges

Mixed bed deionized resin

Ionic Form, H/OH

Percent conversion: Hydrogen 99% minimum, Hydroxide 95% minimum

Cartridge material, polypropylene

Gaskets, Buna-N

###### Piping to be ¾” polyvinylchloride (PVC), schedule 80

###### Mounting bracket included, quantity 2, powder coated steel

Include galvanized bolts to secure housing to brackets

###### Isolation valves, inlet/outlet service

Full port, true union ball valves, ¾”

PVC/EPDM construction

##### Operating conditions

###### Inlet water temperature: 40-100°F (4.4-37.8 °C)

###### Inlet pressure: 10-100 psi (69-690 kPa)

###### Maximum flow rate: 1.25 gpm (0.08 l/s)

###### Inlet voltage:120VAC

###### Water quality effluent: 14-18 Meg Ohm

###### Single Cartridge capacity 1,850 grains as CaCO3:

| Feed Water Quality (ppm TDS) | Feed Water Quality (µS/cm) | Approximate throughput on primary cartridge (gallons /liters) |
| --- | --- | --- |
| 5 | 8 | 6327 (23950) |
| 10 | 15 | 3164 (11977) |
| 20 | 31 | 1582 (5988) |
| 50 | 77 | 633 (2396) |
| 100 | 154 | 316 (1196) |
| 200 | 308 | 158 (598) |
| 300 | 462 | 105 (397) |
| 400 | 615 | 79 (299) |
| 500 | 769 | 63 (238) |
| 750 | 1154 | 42 (159) |
| 1000 | 1538 | 32 (121) |

#### 2.2 	Options: User interface

##### LED Light: Assembly with LED light for indication of throughput

###### Setpoint 50K-Ohms.

###### 120VAC input power

##### Controller

###### Microprocessor controller, Myron L 750 series

###### 3 ½ Digit LCD display

###### +/- 1% of full scale accuracy

###### Alarm contact rating: SPDT 10 amp

###### 120VAC input

###### Water resistivity sensor model CS10, ¾” connection

### PART 3 — EXECUTION

#### 3.1	Installation

##### Install per manufacturer's printed instructions and as indicated on drawings.

##### Coordinate electrical connections as specified in Division 26.

#### 3.2	Commissioning

##### The complete DI systems, as described above, shall be fully commissioned by factory-trained technicians. Commissioning of DI systems shall be coordinated with commissioning of the building automation system.

- END OF SECTION