# SECTION 23 84 13

# CRUV® Electric Evaporative Steam Humidification System

### PART 1 — GENERAL

#### 1.1	Summary

##### Section includes:

###### DRI-STEEM® Corporation, CRUV model, electric steam humidifier

##### Related items:

###### Electrical: Division 26

#### 1.2	References

##### Certifications:

###### ETL, C-ETL

#### 1.3	Submittals

##### Comply with Submittal Procedures and Execution and Closeout Requirements in General Requirements.

##### Submit product data (manufacturer’s specifications, and technical data including performance, construction, and fabrication) for each manufactured component.

#### 1.4	warranty

##### Product shall be warranted to be free from defects in materials and fabrication for a period of two years after installation or 27 months from ship date.

### PART 2 — PRODUCTS

#### 2.1	Humidifier shall be DRI-STEEM CRUV Electric Evaporative Steam Humidification System or engineer-approved equal.

##### Fabrication requirements:

###### Cleanable vaporizing chamber and cover shall be 18- and 14-gauge 304-stainless steel with Heli-arc welded seams. Cover shall be gasketed and quick to remove with threaded Phillips head bolts.

###### Control cabinet shall house electrical devices and shall be secured to prevent accidental contact with electrical components.

###### Water supply and drain connections shall have unions and plugs to allow convenient removal of the evaporating chamber for cleaning.

###### Steam outlet on top of tank shall be configured to connect to hose or pipe

##### Immersion heater(s): Heater(s) shall be Incoloy alloy-sheathed resistance type designed for no more than 86 watts per square inch and shall be mounted on the vaporizing chamber’s removable cover.

##### Over-temperature switch: A factory-mounted and -wired UL-listed limit control sensor with manual reset shall sense an over-temperature condition and de-energize heater circuit controls.

##### Water requirements: The humidifier shall be capable of generating steam from tap, softened, or DI/RO water.

##### Drain: An electric drain valve shall be mounted on humidifier assembly.

#### 2.2	humidifier Options

##### Options for use with DI/RO water:

###### Humidifier shall have a stainless steel manually operated drain valve and a stainless steel float operated fill valve (standard on DI/RO models).

###### Humidifier shall have a stainless steel electric operated drain valve and a stainless steel float operated fill valve with an electric solenoid to prevent tank from filling when the tank drains automatically at the end of a humidification season.

##### 316 stainless steel option: Cleanable vaporizing chamber shall be 316 stainless steel with Heli-arc welded seams.

#### 2.3	humidifier Controls

##### On-off control: Humidifier shall have an electronic water control that shall control automatic refill, low water cutoff and field adjustable autodrain functions. The control system shall include:

###### Water level sensing unit comprised of three metallic probes screwed into a threaded probe head

###### Probe head mounted on the vaporizing chamber

###### A solenoid operated water fill valve factory mounted on humidifier

###### An electronic timer that accumulates operational time (field adjustable to 20, 40, or 80 hours) before an electric drain valve is activated to initiate auto drain function.

#### 2.4	humidifier Control Options

##### Vapor-logic® microprocessor controller with the following features or functions:

###### Web interface and server, included standard on all models:

Web interface shall have same functionality as Vapor-logic keypad/display

Web interface shall allow multiple remotely located users to simultaneously view system operation and/or change system parameters.

Web interface shall have password-protected secure access.

Web interface shall be compatible with standard Internet browsers.

Web interface shall connect directly to a personal computer or through a system network via Ethernet cable.

Automatic cable configuration shall allow straight-through or crossover cables.

Interoperable with any Modbus® network

###### Redundant over-temperature safety control

###### Fully modulating (0% to100%) control of humidifier outputs

###### PID control capability with field-adjustable settings

###### Temperature sensor: A factory mounted sensor, with a temperature range of -40 to 248 (F (-40 to 120 (C) mounted on the humidifier to enable the following functions:

Maintain the evaporating chamber water temperature above freezing

Maintain a user-defined preset evaporating chamber water temperature

Allow rapid warm-up of water in evaporating chamber after a call for humidity, providing 100% operation until steam production occurs

###### USB port on the control board for software updates, data backups, and data restoration

###### Up-time optimizer function to keep humidifier(s) operating through conditions such as fill, drain, or run-time faults, as long as safety conditions are met, minimizing production down-time

###### Real-time clock to allow time-stamped alarm/message tracking, and scheduled events

###### Factory commissioning of humidifier and control board, including system configuration as-ordered

###### Keypad/display operable within a temperature range of 32 to 158 (F (0 to 70 (C), and that provides backlighting for viewing in low light

###### Alarms, unit configuration, and usage timer values shall remain in nonvolatile memory indefinitely during a power outage.

###### The capability to monitor, control, and/or adjust the following parameters:

Relative humidity (RH) set point, actual conditions in the space (from humidity transmitter), RH offset

Dew point set point, actual conditions in the space (from dew point transmitter), dew point offset

Relative humidity (RH) duct high limit set point (switch) and actual conditions

Relative humidity (RH) duct high limit set point, actual conditions (from transmitter), high limit span, and high limit offset

Total system demand in % of humidifier capacity

Total system output in lbs/hour (kg/h)

Drain/flush duration

End-of-season drain status (on standard water systems and if ordered as a DI water option) and hours humidifier is idle before end of season draining occurs

Window glass surface temperature (in % RH offset application using sensor ordered as an option) with programmable offset

Air temperature or other auxiliary temperature monitoring with programmable offset (using sensor ordered as an option)

System alarms and system messages, current and previous

Adjustable water skim duration

Programmable outputs for remote signaling of alarms and/or messages, device activation (such as a fan), or for signaling tank heating and/or steam production

System diagnostics that include:

Test outputs function to verify component operation

Test humidifier function, by simulating demand to validate performance

Data collection of RH, air temperature, water use, energy use, alarms, and service messages for viewing from the keypad/display or Web interface

Service notification scheduling

Password-protected system parameters

Keypad/display or Web interface displays in English, French, or German languages

Numerical units displayed in inch-pound or SI units

###### Interoperability using LonTalk.

###### Interoperability using BACnet MS/TP.

##### Water level control for softened or hard water:

###### Automatic refill, low water cutoff, field-adjustable skimmer bleedoff functions and automatic drain-down of humidifier. System shall consist of:

A water level sensing unit comprised of three metallic probes screwed into a threaded probe head. Probe head shall incorporate probe isolation chamber to eliminate short-circuiting between probes caused by mineral coating of probe head. Probe head shall be mounted on the humidifier assembly.

A solenoid operated fill valve factory mounted on the humidifier assembly

End-of-season drain automatically drains humidifier tank after a user-defined period of system inactivity (Vapor-logic controller only).

##### Water level control for DI/RO water:

###### System shall provide for continuous control of water level and will accommodate the use of deionized or reverse osmosis water with resistance up to 18 M-ohm/cm.

###### System shall:

Have a water level sensing unit comprised of a float operated stainless steel valve for water makeup

Have a low water cutoff float switch

Operate within inlet water pressure range of 25 to 80 psi (172 to 552 kPa)

##### Time-proportioning (TP) modulation control: The humidifier shall cycle a single output on and off corresponding to an input demand signal (Vapor-logic controller only).

##### SSR modulating control option: Humidifier shall have an electronic power controller, surface mounted and wired in humidifier control cabinet assembly to regulate current to humidifier load. This regulation will modulate between 0% to 100% of maximum capacity. (Vapor-logic controller only)

##### Option keypad cable lengths: Available cable lengths: 5’ (1.5 m), 10’ (3 m), 25' (7.6 m), 50' (15 m), 100' (30 m), or 500' (152 m)

##### Control input accessory options:

###### Humidity transmitter, room: Humidity transmitter shall be a room-mounted device that measures from 0% to 100% of RH range and provides a linear output (10% to 90% RH) from 4 to 20 mA. Accuracy ± 2% RH. Supply voltage 21 VDC. Operating temperature range: -4 to 140 (F (-20 to 60 (C).

###### Humidity transmitter, duct: Humidity transmitter shall be a duct-mounted device that measures from 0% to 100% RH range and provides a linear output (10% to 90% RH) from 4 to 20 mA. Accuracy ± 2% RH. Supply voltage 21 VDC. Operating temperature range: -4 to 140 (F (-20 to 60 (C).

###### Auxiliary temperature sensor/transmitter: Auxiliary temperature sensor and transmitter shall allow air temperature monitoring, such as in a duct, and shall enable temperature compensation to prevent window condensation. Temperature transmitter, operating temperature range of -20 to 160 (F (-29 to 71 (C), shall be provided for field installation. Transmitter shall supply its signal (4 to 20 mA) to the microprocessor control system, which shall lower the indoor RH set point to a level 5% or more below the dew point temperature during a cold spell, thus preventing window condensation. The indoor RH shall be automatically returned to the normal setting when the glass temperature rises.

###### Humidistat, on-off, room: Electric humidistat control shall be an on-off style, room-mounted with a control range of 10% to 90% RH. Compatible with 24, 120, and 240 VAC. Operating temperature range 40 to 125 (F (4 to 52 (C).

###### Humidistat, on-off, duct: Electric humidistat control shall be an on-off style, duct mounted with a control range of 15% to 95% RH. Compatible with 24, 120, and 240 VAC. Operating temperature range 40 to 125 (F (4 to 52 (C).

###### Humidistat, on-off, high limit: Electric humidistat control shall be an on-off style, duct mounted with a control range of 15% to 95% RH. Compatible with 24, 120, and 240 VAC. Operating temperature range 40 to 125 (F (4 to 52 (C).

###### Modulating high limit control: The modulating high limit control system shall include a modulating electronic humidity transmitter (duct-mounted downstream from the humidifier). It shall transmit to the microprocessor controller to modulate humidifier output and maintain the highest desired space humidity possible, at all airflow volumes, without saturation of the airstream. (For this application, it is recommended to use a sail type airflow-proving switch.)

###### Airflow proving switch, pressure type: Airflow proving switch shall be diaphragm-operated with pitot tube for field installation. Switch shall have an adjustable control point range of 0.05" wc to 12" wc (12.5 to 2988 Pa) Operating temperature range -40 to 180 (F (-40 to 82 (C). Compatible with 24, 120, and 240 VAC.

###### Airflow proving switch, sail type: Airflow proving switch shall be a sail-operated electric switch for field installation. Switch makes @ 250 fpm (1.3 m/s), breaks @ 75 fpm (0.4 m/s). Maximum operating temperature for sail: 170 (F (77 (C). Maximum operating temperature for switch: 125 (F (52 (C).

#### 2.5	humidifier Accessories

##### Pump, low-flow, high-temperature: Pump shall be suitable for pumping water up to 212 (F (100 (C). Maximum pump flow rate shall be 3.8gpm (228 gph) with a 12-foot head (36 kPa). Pump shall have a 1-gallon cast aluminum reservoir with a 3/8" pipe thread (DN10) outlet connection, two 1-1/4" (DN32) inlet openings, and integral float switch. Pump shall be used with 115 VAC. Pump also available with 230 VAC. Pump shall be UL recognized and wired per NEC requirements.

##### Pump, high-flow, high-temperature: Pump shall be suitable for pumping water up to 212 (F (100 (C). Maximum pump flow rate shall be 55 gpm (3300 gph) with a 12-foot head (36 kPa). Pump shall have a 4-gallon cast aluminum reservoir with vapor seal, a 3/4" pipe thread (DN20) outlet connection, a 1-1/2" pipe thread (DN40) inlet connection, and integral float switch. Pump shall be used with 115 VAC. Pump can be wired for use with 115/230 VAC. Pump shall be UL recognized and wired per NEC requirements.

##### Pump, high-flow, low-temperature: Pump shall be suitable for pumping water up to 150 (F (65.5 (C). Maximum pump flow rate shall be 55 gpm (3300 gph) with a 12-foot head (36 kPa). Pump shall have a 2-gallon cast aluminum reservoir, a 1" pipe thread (DN25) outlet connection, a 1-1/2" pipe thread (DN40) inlet connection, and integral float switch. Pump shall be used with 115 VAC. Pump can be wired for use with 115/230 VAC. Pump shall be UL recognized and wired per NEC requirements.

##### Drane-kooler: A thermostatically controlled water valve shall meter an amount of cold water into a stainless steel mixing chamber to temper 212 (F (100 (C) water with a 6 gpm (0.38 l/s) in-flow rate to a 140 (F (60 (C) discharge temperature to sanitary system.

#### 2.6 	Humidifier Dispersion Options

##### Ultra-sorb® steam dispersion panel:

###### The factory-assembled steam dispersion panel shall include the following components:

Steam supply header/separator

Condensate collection header

Closely-spaced steam dispersion tubes spanning the distance between the two headers

###### Each dispersion tube shall be fitted with two rows of steam discharge tubelets inserted into the tube wall, centered on the diametric line, and spaced 1-1/2" (38 mm) apart. Each tubelet shall be made of a thermal-resin material designed for high steam temperatures. The two rows of tubelets in each dispersion tube shall discharge steam in diametrically opposite directions, perpendicular to airflow.

###### Each tubelet shall extend through the wall of and into the center of the dispersion tube and contain a steam orifice sized for its required steam capacity.

###### The humidifier shall provide absorption characteristics that preclude water accumulation on any in-duct surface within _____" (_____ mm) of the humidifier tube panel while maintaining conditions of _____% maximum relative humidity at a minimum of _____(F (_____(C) in the duct airstream.

###### Air pressure loss across the humidifier panel shall not exceed _____" water column (_____ Pa) at a duct air velocity of _____fpm (_____m/s).

###### Each packaged humidifier panel assembly of tubes and headers shall be contained within a galvanized metal casing to allow convenient duct mounting, or to facilitate the stacking of and/or the end-to-end mounting of multiple humidifier panels in ducts or air handler casings. When so designated, the humidifier panel shall be shipped unassembled.

###### All tubes and headers shall be 304 stainless steel and be Heli-arc welded.

###### Tubes shall be joined to headers with slip-fit couplings.

###### Option: Tubes shall be joined to headers with EPDM hose cuffs with nylon clamps.

###### Option: Casing assembly shall be 304 stainless steel.

###### Option: Tubes and headers shall be 316 stainless steel and be Heli-arc welded.

###### Option: High-efficiency dispersion tubes

Dispersion tubes shall be insulated with a plenum-approved insulating material for in-duct installation and have an R-value not less than 0.5 at a thickness not more than 0.125" (3.2 mm), for minimal increase in dispersion tube diameter.

Airstream heat gain shall not exceed the values as scheduled; the values shall be supported by the manufacturer's published data.

Insulating material shall meet the following criteria at 0.125" (3.2 mm) thickness:

Fire/smoke index shall be 0/0 per any of the following test procedures:
-  UL 723 fire/smoke index (Test for Surface Burning Characteristics of Building Materials) 
-  NFPA 255 (Standard Method of Test of Surface Burning Characteristics of Building
    Materials)
-  ASTM E84 (Surface Burning Characteristics for Materials Used in Plenums)

Stable up to 300 °F (148 °C) continuous — to prevent material degradation, hardening, or crumbling at high temperatures

Closed-cell construction does not absorb water or support microbial growth — to negate the need for vapor barriers and jackets

Non-toxic and pure as documented in manufacturer's data — to prevent off-gassing and to facilitate use in clean rooms, pharmaceutical applications, and food industries

Will not degrade when exposed to UVC light — to negate the need for UV wraps

Continuous, seam-welded, and held in place without bands or clamps — to minimize surfaces for the accumulation of particulate matter

##### Rapid-sorb® dispersion panel:

###### Each tube bank shall consist of a horizontal header/separator and designated quantity of vertical dispersion tubes necessary to achieve the required steam capacity and absorption distance.

###### The humidifier shall provide absorption characteristics that preclude water accumulation on any in-duct surface within _____" (_____ mm) of the humidifier tube panel while maintaining conditions of _____% maximum relative humidity at a minimum of _____(F (_____(C) in the duct airstream.

###### Air pressure loss across the humidifier panel shall not exceed _____" water column (_____ Pa) at a duct air velocity of _____fpm (_____m/s).

###### Header/separator shall span the width of the duct, be constructed of stainless steel and be fitted with connections for dispersion tubes.

The dispersion tubes shall extend the height of the duct and shall be fitted with two rows of tubelets on the diametric centerline and spaced 1-1/2" (38 mm) apart.

Each tubelet shall be made of a thermal-resin material designed for high steam temperatures.

Each tubelet shall extend through the wall of and into the center of the dispersion tube and contain a steam orifice sized for its required steam capacity.

For securing the upper ends of the tubes, a 3/4" x 2" (19 mm x 50 mm) stainless steel L-bracket shall be furnished, which the installer shall attach to the duct or housing.

###### Option: High-efficiency dispersion tubes

Dispersion tubes shall be insulated with a plenum-approved insulating material for in-duct installation and have an R-value not less than 0.5 at a thickness not more than 0.125" (3.2 mm), for minimal increase in dispersion tube diameter.

Airstream heat gain shall not exceed the values as scheduled; the values shall be supported by the manufacturer's published data.

Insulating material shall meet the following criteria at 0.125" (3.2 mm) thickness:

Fire/smoke index shall be 0/0 per any of the following test procedures:
-  UL 723 fire/smoke index (Test for Surface Burning Characteristics of Building Materials) 
-  NFPA 255 (Standard Method of Test of Surface Burning Characteristics of Building
    Materials)
-  ASTM E84 (Surface Burning Characteristics for Materials Used in Plenums)

Stable up to 300 °F (148 °C) continuous — to prevent material degradation, hardening, or crumbling at high temperatures

Closed-cell construction does not absorb water or support microbial growth — to negate the need for vapor barriers and jackets

Non-toxic and pure as documented in manufacturer's data — to prevent off-gassing and to facilitate use in clean rooms, pharmaceutical applications, and food industries

Will not degrade when exposed to UVC light — to negate the need for UV wraps

Continuous, seam-welded, and held in place without bands or clamps — to minimize surfaces for the accumulation of particulate matter

##### Single tube dispersion:

###### Dispersion tube(s) shall be fabricated of stainless steel tubing with uniformly spaced tubelets for steam dispersion. Each tubelet shall be made of a thermal-resin material designed for high steam temperatures. Each tubelet shall extend through the wall and to the center of dispersion tube and incorporate a properly sized calibrated orifice.

###### Dispersion tube(s) shall be pitched 2"/ft (15%) toward humidifier to allow condensate to return to humidifier.

##### Single tube dispersion with condensate drain:

###### Dispersion tube(s) shall be fabricated of stainless steel tubing with uniformly spaced tubelets for steam dispersion. Each tubelet shall be made of a thermal-resin material designed for high steam temperatures. Each tubelet shall extend through the wall and to the center of dispersion tube and incorporate a properly sized calibrated orifice.

###### Dispersion tube(s) shall be pitched 1/8"/ft (1%) minimum toward the condensate drain to allow condensate to leave the dispersion tube via the condensate drain tube.

###### The condensate drain tube shall be stainless steel tubing.

### PART 3 — EXECUTION

#### 3.1	Installation

##### Install per manufacturer's printed instructions and as indicated on drawings.

##### Coordinate electrical connections as specified in Division 26.

END OF SECTION

# Text boxes

Specifier note: Select appropriate humidifier options from lists below. See also Section 2.3 Humidifier Controls, Section 2.4 Humidifier Control Options, Section 2.5 Humidifier Accessories, and Section 2.6 Humidifier Dispersion Options.