SECTION 23 84 13

Ultra-sorb® Models LV and LH Steam Dispersion Panel Humidifiers

### PART 1 – GENERAL

#### 1.1	Summary

##### Section includes:

###### DRI-STEEM Corporation, Ultra-sorb steam dispersion panels

#### 1.2	References

##### Certifications

###### OSHPD Special Seismic Pre-approval

###### IBC 2009 Seismic Qualification

#### 1.3	Submittals

##### Comply with Submittal Procedures and Execution and Closeout Requirements in General Requirements.

##### Submit product data (manufacturer’s specifications and technical data including performance, construction, and fabrication) for each manufactured component.

#### 1.4	Warranty

##### Product shall be warranted to be free from defects in materials and fabrication for a period of two years after installation or 27 months from ship date.

### PART 2 – PRODUCTS

#### 2.1	Humidifier shall be DRI-STEEM Ultra-sorb Steam Dispersion Panel or engineer-approved equal.

##### The Ultra-sorb Models LV and LH steam dispersion panel shall directly inject pressurized boiler steam or evaporative, non-pressurized steam into ducted air for humidification.

##### Steam, dispersion panels shall be factory-assembled and include the following components:

###### Steam supply header/separator

###### Condensate collection header

###### Closely-spaced steam dispersion tubes spanning the distance between the two headers

##### Each dispersion tube shall be fitted with two rows of steam discharge tubelets inserted into the tube wall, centered on the diametric line, and spaced 1.5" (38 mm) apart. Each tubelet shall be made of a thermal-resin material designed for high steam temperatures. The two rows of tubelets in each dispersion tube shall discharge steam in diametrically opposite directions, perpendicular to airflow.

##### Each tubelet shall extend through the wall of and into the center of the dispersion tube and contain a steam orifice sized for its required steam capacity.

##### The humidifier shall provide absorption characteristics that preclude water accumulation on any in-duct surface within _____" (_____ mm) of the humidifier tube panel while maintaining conditions of _____% maximum relative humidity (RH) at a minimum of _____(F (_____(C) in the duct airstream.

##### Air pressure loss across the humidifier panel shall not exceed _____" water column (_____ Pa) at a duct air velocity of _____fpm (_____m/s).

##### Each packaged humidifier panel assembly of tubes and headers shall be contained within a galvanized metal casing to allow convenient duct mounting, or to facilitate the stacking of and/or the end-to-end mounting of multiple humidifier panels in ducts or air handler casings. When so designated, the humidifier panel shall be shipped unassembled.

##### All tubes and headers shall be 304 stainless steel, and welded joints shall be Heli-arc welded.

##### Tubes shall be joined to headers with slip-fit couplings to facilitate easy removal.

##### Steam trap(s):

###### Humidifier shall have one or two float and thermostatic (F&T) traps.

#### 2.2	Humidifier Options

##### Optional stainless steel components:

###### Inlet strainer shall be stainless steel.

###### Entire valve shall be stainless steel.

###### Tubes and headers shall be 316 stainless steel and be Heli-arc welded.

###### Casing assembly shall be 304 stainless steel.

###### Headers shall be 316 stainless steel and be Heli-arc welded.

##### Valve options:

###### Modulating pneumatic humidification steam control valve and actuator: Valve shall be a normally closed modulating type with modified linear flow. Valve trim shall be stainless steel, and sized to meet humidification requirements. Actuator shall be a pneumatic type to modulate the steam valve in response to a variable pneumatic signal demand, and be direct acting.

###### Modulating electronic humidification steam control valve: Valve shall be a normally closed with an electronic actuator. Valve trim shall be stainless steel, and sized to meet humidification requirements. Actuator shall respond to a variable electronic signal. Available signal inputs: 4 to 20 mA, 2 to 10 VDC.

###### Pilot positioner: The valve pneumatic actuator shall be equipped with an adjustable pilot positioner.

##### High-efficiency dispersion tube option:

###### Dispersion tubes shall be insulated with a plenum-approved insulating material for in-duct installation and have an R-value not less than 0.5 at a thickness not more than 0.125" (3.2 mm), for minimal increase in dispersion tube diameter.

###### Airstream heat gain shall not exceed the values as scheduled; the values shall be supported by the manufacturer's published data.

###### Insulating material shall meet the following criteria at 0.125" (3.2 mm) thickness:

Fire/smoke index shall be 0/0 per any of the following test procedures:
-  UL 723 fire/smoke index (Test for Surface Burning Characteristics of Building Materials) 
-  NFPA 255 (Standard Method of Test of Surface Burning Characteristics of Building Materials)
-  ASTM E84 (Surface Burning Characteristics for Materials Used in Plenums)

Stable up to 300 °F (148 °C) continuous — to prevent material degradation, hardening, or crumbling at high temperatures

Closed-cell construction does not absorb water or support microbial growth — to negate the need for vapor barriers and jackets

Non-toxic and pure as documented in manufacturer's data — to prevent off-gassing and to facilitate use in clean rooms, pharmaceutical applications, and food industries

Will not degrade when exposed to UVC light — to negate the need for UV wraps

Continuous, seam-welded, and held in place without bands or clamps — to minimize surfaces for the accumulation of particulate matter

##### Humidifier shall meet OSHPD Special Seismic Pre-approval for a SDS = 2.0 g for AHU applications and SDS = 2.5 g for duct applications.

##### Humidifier shall meet IBC 2009 Seismic Qualification by shake table testing for a SDS = 2.0 g for AHU applications and SDS = 2.5 g for duct applications.

#### 2.3	Humidifier Control Options

##### Control input accessory options:

###### Humidistat, electronic, room: Electronic humidistat shall be room-mounted and produce a modulated DC signal output, field-selectable 0 to 10 VDC or 6 to 9 VDC with control action field-selectable to be direct or reverse acting. Set point range 20% to 80% RH, supply voltage 24 DC or 24 AC. Maximum ambient temperature 122 (F (50 (C).

###### Humidistat, pneumatic, room: The pneumatic room humidistat shall provide a pneumatic modulating output in response to humidity changes, approximate range 10% to 95% RH, maximum inlet pressure 25 psi (172 kPa). Operating temperature range 40 to 150 (F (4 to 66 (C). Provided with mounting bracket and cover.

###### Humidistat, pneumatic, duct: The pneumatic duct humidistat shall provide a pneumatic modulating output in response to humidity changes. Preset at 35% RH set point. Maximum inlet pressure 25 psi (172 kPa). Maximum air velocity 2000 fpm (10 m/s). Operating temperature range 20 to 150 (F 
(-7 to 66 (C).

###### Humidistat, pneumatic high limit, duct: The pneumatic duct high limit humidistat shall provide a pneumatic modulating output in response to humidity changes. Preset at 85% RH set point. Maximum inlet pressure 25 psi (172 kPa). Maximum air velocity 2000 fpm (10 m/s). Operating temperature range 20 to 150 (F (-7 to 66 (C).

###### Airflow proving switch, pressure type: Airflow proving switch shall be diaphragm-operated with pitot tube for field installation. Switch shall have an adjustable control point range of 0.05" to 12" wc 
(12.5 to 2988 Pa). Operating temperature range -40 to 180 (F (-40 to 82 (C). Compatible with 24, 120, and 240 VAC.

###### Airflow proving switch, sail type: Airflow proving switch shall be a sail-operated electric switch for field installation. Switch makes at 250 fpm (1.3 m/s), and breaks at 75 fpm (0.4 m/s). Maximum operating temperature for sail: 170 (F (77 (C). Maximum operating temperature for switch: 125 (F (52 (C)

###### Airflow proving switch, pneumatic type: The pneumatic airflow switch shall detect the presence or absence of airflow. Field-installed in duct. Maximum air velocity 2000 fpm (10 m/s). Switch action vents air on no-flow. Maximum pneumatic inlet pressure 20 psi (138 kPa). Operating temperature range 32 to 180 (F (0 to 82 (C).

#### 2.4	Humidifier Accessories

##### Drane-kooler. A thermostatically controlled water valve shall meter an amount of cold water into a stainless steel mixing chamber to temper 212 (F (100 (C) water with a 6 gpm (0.38 L/s) in-flow rate to a 140 (F (60 (C) discharge temperature to sanitary system.

### PART 3 – EXECUTION

#### 3.1	Installation

##### Install per manufacturer's printed instructions and as indicated on drawings.

##### Coordinate electrical connections specified in Division 26.

END OF SECTION