- SECTION 23 84 13

- Vaporstream® Electric Evaporative Steam Humidification System

### PART 1 — GENERAL

#### 1.1	Summary

##### Section includes:

###### DRI-STEEM Corporation, Vaporstream model, electric steam humidifier

##### Related items:

###### Electrical Service and Connections: Division 26

#### 1.2	References

##### Certifications:

###### ETL, C-ETL

###### CE

###### OSHPD Special Seismic Certification Preapproval

###### IBC 2009 Seismic Qualification

#### 1.3	Submittals

##### Comply with Submittal Procedures and Execution and Closeout Requirements in General Requirements.

##### Submit product data (manufacturer’s specifications, and technical data including performance, construction and fabrication) for each manufactured component.

#### 1.4	Warranty

##### Product shall be warranted to be free from defects in materials and fabrication for a period of two years after installation or 27 months from ship date.

### PART 2 — PRODUCTS

#### 2.1	Humidifier shall be Vaporstream Electric Evaporative Steam Humidification System or engineer-approved equal.

##### Fabrication requirements:

###### Tank and cover: 14- and 12-gauge 304-stainless steel with Heli-arc welded seams

###### Quick removable cover with threaded knobs and gasketed flanges

###### Heater cover interlock safety switch: A factory-mounted and wired interlock safety switch shall de-energize the heaters when the heater cover is removed.

###### Terminal strip to allow all control wiring connections at the humidifier to be made in a single location

###### Easily accessible cleanout plate

###### Steam outlet on top of tank cover to connect to hose, pipe or flange connection

##### Immersion heater(s): Heater(s) shall be Incoloy alloy-sheathed resistance type designed for no more than 86 watts per square inch. Two threaded ends of each heater element shall pass through the top of the evaporating chamber and be secured and sealed with washer and threaded nuts to evaporating chamber.

##### Temperature sensor: A factory mounted sensor, with a temperature range of -40 to 248 F (-40 to 120 C) shall be mounted on the humidifier to enable the following functions:

###### Maintain the evaporating chamber water temperature above freezing

###### Maintain a user-defined preset evaporating chamber water temperature

###### Allow rapid warm-up of water in evaporating chamber after a call for humidity, providing 100% operation until steam production occurs

###### Provide backup over-temperature protection for the over-temperature switch

##### Over-temperature switch: A factory-mounted and -wired UL-listed limit control sensor with manual reset shall sense an over-temperature condition and de-energize heater circuit controls.

##### Mounting: Humidifier shall be mounted on a pair of trapeze hangers with 3/8" threaded steel rods, hardware and two predrilled pieces of angle iron (models 6-1 through 100-4), or the humidifier shall be mounted on a provided angle-iron suspension structure (models 2-1 through 5-1).

##### Water requirements: The humidifier shall be capable of generating steam from tap, softened or DI/RO water.

##### Drain: An electric drain valve shall be mounted on humidifier assembly to allow tank to drain automatically at the end of a humidification season (standard water models only).

Specifier note: Select appropriate humidifier options from lists below. See also Section 2.3 Humidifier Controls, Section 2.4 Humidifier Control Options, Section 2.5 Accessories, and Section 2.6 Humidifier Dispersion Options.

#### 2.2	Humidifier Options

##### Fabrication options:

###### Tank and cover shall be 316 stainless steel with Heli-arc welded seams.

###### Factory insulation: Humidifier shall be covered with 1"-thick (25 mm), rigid, foil-faced fiberglass insulation. All surfaces except front face panel and heater terminal cover shall have insulation.

###### Seismic Certification option: Humidifier shall meet OSHPD Special Seismic Certification Preapproval 
for SDS = 2.5 g (floor mount or weather cover only). Includes seismic leg assembly and mounting hardware.

###### Humidifier shall meet IBC 2009 Seismic Qualification by shake table testing for a SDS = 2.5 g (floor mount or weather cover only). Includes seismic leg assembly and mounting hardware.

##### Mounting options:

###### Support legs: Humidifier shall have four painted angle-iron support legs that provide 24" (610 mm) minimum clearance between underside of humidifier and floor (not available for single-heater models).

###### Wall brackets: Humidifier shall have two welded and painted steel wall brackets to support humidifier on a vertical surface (not available for single-heater models; mounting on steel stud walls is not recommended for 9- and 12-heater models).

##### Options for use with DI/RO water:

###### Humidifier shall have a stainless steel manually operated drain valve and a stainless steel float operated fill valve (standard on DI/RO models).

###### Humidifier shall have a stainless steel electric operated drain valve and a stainless steel float operated fill valve with an electric solenoid to prevent tank from filling when the tank drains automatically at the end of a humidification season.

##### Outdoor enclosure system:

###### Factory assembled and tested with the humidifier installed to provide complete weather protection and to operate within the following temperature limits:  -40 to 120 F (-40 to 50 C).

###### Humidifier and outdoor enclosure shall be shipped as one unit.

###### Frame construction: 5" (127 mm), 14-gauge, G-90 galvanized steel formed frame, suitably reinforced and braced to permit loading, shipping, unloading and rigging to the unit destination without damage to external or internal components. The base frame shall be corrosion resistant without painting or further coating.

###### Housing construction: 14-gauge, G-90 galvanized steel panels fabricated into self-framing, double standing seam-type construction. All joints shall be caulked weather-tight with a silicone sealant. All interior surfaces shall be insulated with 1" (25 mm), 2.2 lbs/sq ft (10.8 kg/m2) rigid, noncombustible glass fiber insulation. No exposed insulation shall be permitted on the top-wearing surface of the floor of the unit. The floor shall be insulated from underneath. The floor shall have a drain connection.

###### Access door construction: Access door shall provide access to all internal components, be constructed of 14-gauge, G-90 galvanized steel with a gasket around the full perimeter of the doorframe, with heavy-duty stainless steel hinges, and latches.

###### Ventilation fan: wired to a thermostat to ventilate the control cabinet and the enclosure.

###### Heaters:

The enclosure shall have thermostatically-controlled heaters to ensure proper operation during cold weather.

Outdoor enclosure without heaters option: The outdoor enclosure shall be provided without electric heaters, control thermostat and wiring.

###### Roof curb option: The roof curb shall be manufactured of 14-gauge, galvanized steel and provided with necessary hardware for bolt-together assembly. The curb is to be a minimum of 14" (356 mm) high. A 1" (25 mm) by 1/4" (6 mm) closed cell curb gasket with adhesive on one side is to be supplied with the hardware.

###### Internal steam vapor plumbing option: The outdoor enclosure shall have piping to discharge steam through the base of the unit.

##### Outdoor weather cover option: Humidifier shall have an outdoor weather cover assembly that is an ETL-recognized component, and that has been tested to meet UL 1995 and CSA C22.2 No. 236 standards. Weather cover shall be factory-assembled.

#### 2.3	Humidifier Controls

##### Time-proportioning (TP) modulation control: The humidifier shall cycle a single output on and off corresponding to an input demand signal.

##### Control cabinet: NEMA-12 control cabinet shall be shipped loose. An ETL/C-ETL listed control cabinet assembly comprising control devices shall be mounted on a subpanel. Control devices shall include a Vapor-logic®4 microprocessor control system, a magnetic contactor for each heating stage, a control circuit transformer, a fuse set for each heating stage (for multiple heat stages only), a numbered terminal strip, and all interconnecting wiring. All wiring diagrams shall be included in the control cabinet.

##### Vapor-logic microprocessor controller with the following features or functions:

###### Web interface and server, included standard on all models:

Web interface shall have same functionality as Vapor-logic keypad/display

Web interface shall allow multiple remotely located users to simultaneously view system operation and/or change system parameters.

Web interface shall have password-protected secure access.

Web interface shall be compatible with standard Internet browsers.

Web interface shall connect directly to a personal computer or through a system network via Ethernet cable.

Automatic cable configuration shall allow straight-through or crossover cables.

###### Interoperable with any Modbus® network

###### Redundant over-temperature safety control

###### Fully modulating (0% to100%) control of humidifier outputs

###### PID control capability with field-adjustable settings

###### Water level control for softened or hard water:

Automatic refill, low water cutoff, field-adjustable skimmer bleedoff functions and automatic drain-down of humidifier. System shall consist of:

A water level sensing unit comprised of three metallic probes screwed into a threaded probe head. Probe head shall incorporate probe isolation chamber to eliminate short-circuiting between probes caused by mineral coating of probe head. Probe head shall be mounted on the humidifier assembly.

A solenoid operated fill valve factory mounted on the humidifier assembly

End-of-season drain automatically drains humidifier tank after a user-defined period of system inactivity.

###### Temperature sensor: A factory mounted sensor, with a temperature range of -40 to 248 F (-40 to 120 C) mounted on the humidifier to enable the following functions:

Maintain the evaporating chamber water temperature above freezing

Maintain a user-defined preset evaporating chamber water temperature

Allow rapid warm-up of water in evaporating chamber after a call for humidity, providing 100% operation until steam production occurs

###### USB port on the control board for software updates, data backups, and data restoration

###### Up-time optimizer function to keep humidifier(s) operating through conditions such as fill, drain, or run-time faults, as long as safety conditions are met, minimizing production down-time

###### Real-time clock to allow time-stamped alarm/message tracking, and scheduled events

###### Factory commissioning of humidifier and control board, including system configuration as-ordered

###### Keypad/display operable within a temperature range of 32 to 158 F (0 to 70 C), and that provides backlighting for viewing in low light

###### Alarms, unit configuration, and usage timer values shall remain in nonvolatile memory indefinitely during a power outage.

###### The capability to monitor, control, and/or adjust the following parameters:

Relative humidity (RH) set point, actual conditions in the space (from humidity transmitter), RH offset

Dew point set point, actual conditions in the space (from dew point transmitter), dew point offset

Relative humidity (RH) duct high limit set point (switch) and actual conditions

Relative humidity (RH) duct high limit set point, actual conditions (from transmitter), high limit span, and high limit offset

Total system demand in % of humidifier capacity

Total system output in lbs/hour (kg/h)

Drain/flush duration

End-of-season drain status (on standard water systems and if ordered as a DI water option) and hours humidifier is idle before end of season draining occurs

Window glass surface temperature (in % RH offset application using sensor ordered as an option) with programmable offset

Air temperature or other auxiliary temperature monitoring with programmable offset (using sensor ordered as an option)

System alarms and system messages, current and previous

Adjustable water skim duration

Programmable outputs for remote signaling of alarms and/or messages, device activation (such as a fan), or for signaling tank heating and/or steam production

System diagnostics that include:

Test outputs function to verify component operation

Test humidifier function, by simulating demand to validate performance

Data collection of RH, air temperature, water use, energy use, alarms, and service messages for viewing from the keypad/display or Web interface

Service notification scheduling

Password-protected system parameters

Keypad/display or Web interface displays in English, French, or German languages

Numerical units displayed in inch-pound or SI units

#### 2.4	Humidifier Control Options

##### Interoperability using LonTalk.

##### Interoperability using BACnet MS/TP.

##### Multiple humidifier tank control. Vapor-logic shall be programmed and configured at the factory to control multiple humidifier tanks. Controller functions shall include all Vapor-logic functions listed above plus:

###### The controller shall control up to 16 humidifier tanks.

###### Automatic run-time balancing. The controller shall assign duty to all humidifier tanks in the multi-tank group such that each humidifier accrues approximately the same hours of duty, thereby ensuring equal wear across all humidifiers in the multi-tank group.

###### One humidifier tank shall be capable of being controlled as a redundant tank.

###### One Vapor-logic keypad/display shall be included with each multi-tank group.

##### Control cabinet options:

###### Mounted on humidifier: NEMA-12 control cabinet shall be factory attached to the side of humidifier with all wiring between cabinet and humidifier completed at factory. An ETL/C-ETL listed control cabinet assembly comprising control devices shall be mounted on a subpanel. Control devices shall include a Vapor-logic microprocessor control system, a magnetic contactor for each heat stage, a control circuit transformer, a fuse set for each heating stage (for multiple heat stages only), a numbered terminal strip, and all interconnecting wiring. A wiring diagram shall be included in the control cabinet.

###### NEMA-4 control cabinet: The control cabinet shall be a NEMA-4 enclosure, rated and constructed for outdoor environments.

###### Cabinet door interlock switch: The control cabinet shall have an interlock control switch with manual override to remove control voltage when door is opened.

###### Cabinet door lock: Control cabinet shall have a lock with keys provided.

##### Water level control for DI/RO water:

###### System shall provide for continuous control of water level and will accommodate the use of deionized or reverse osmosis water with resistance up to 18 M-ohm/cm.

###### System shall:

Have a water level sensing unit comprised of a float operated stainless steel valve for water makeup

Have a low water cutoff float switch

Operate within inlet water pressure range of 25 to 80 psi (172 to 552 kPa)

##### Remote keypad option: Provide a keypad with cable for remote mounting. Available cable lengths: 10’ (3 m), 25' (7.6 m), 50' (15 m), 100' (30 m), or 500' (152 m)

##### Keypad mounted on cabinet option: The keypad shall be factory mounted on the side of the control cabinet.

##### Control output options:

###### SSR/sequencer modulation control option: The humidifier shall have a secondary electronic power controller that is mounted and wired through the control cabinet door and modulates a single humidifier output from 0% to 100% while the Vapor-logic controller automatically sequences additional heat stages for humidification as demand requires.

###### 100% SSR modulation control option: The humidifier shall have all humidifier heat stages modulating through electronic power controllers, which provide a total 0% to 100% modulation of humidifier output. All SSR controls are mounted and wired through the cabinet door.

##### Control input accessory options:

###### Humidity transmitter, room: Humidity transmitter shall be a room-mounted device that measures from 0% to 100% of RH range and provides a linear output (10% to 90% RH) from 4 to 20 mA. Accuracy ± 2% RH. Supply voltage 21 VDC. Operating temperature range: -4 to 140 F (-20 to 60 C).

###### Humidity transmitter, duct: Humidity transmitter shall be a duct-mounted device that measures from 0% to 100% RH range and provides a linear output (10% to 90% RH) from 4 to 20 mA. Accuracy ± 2% RH. Supply voltage 21 VDC. Operating temperature range: -4 to 140 F (-20 to 60 C).

###### Dew point transmitter: A dew point transmitter (duct- or room-mounted) shall measure the humidity and temperature in the environment and then compute the dew point. Output 4 to 20 mA (700 ohms maximum). Supply voltage 24 VDC. Operating temperature range when duct-mounted: -40 to 185 F (-40 to 85 C). Operating temperature range when room-mounted: 32 to 122 F (0 to 50 C).

###### Auxiliary temperature sensor/transmitter: Auxiliary temperature sensor and transmitter shall allow air temperature monitoring, such as in a duct, and shall enable temperature compensation to prevent window condensation. Temperature transmitter, operating temperature range -20 to 160 F (-29 to 71 C), shall be provided for field installation. Transmitter shall supply its signal (4 to 20 mA) to the microprocessor control system, which shall lower the indoor RH set point to a level 5% or more below the dew point temperature during a cold spell, thus preventing window condensation. The indoor RH shall be automatically returned to the normal setting when the glass temperature rises.

###### Humidistat, on-off, room: Electric humidistat control shall be an on-off style, room-mounted with a control range of 10% to 90% RH. Compatible with 24, 120, and 240 VAC. Operating temperature range 40 to 125 F (4 to 52 C).

###### Humidistat, on-off, duct: Electric humidistat control shall be an on-off style, duct mounted with a control range of 15% to 95% RH. Compatible with 24, 120, and 240 VAC. Operating temperature range 40 to 125 F (4 to 52 C).

###### Humidistat, on-off, high limit: Electric humidistat control shall be an on-off style, duct mounted with a control range of 15% to 95% RH. Compatible with 24, 120, and 240 VAC. Operating temperature range 40 to 125 F (4 to 52 C).

###### Modulating high limit control: The modulating high limit control system shall include a modulating electronic humidity transmitter (duct-mounted downstream from the humidifier). It shall transmit to the microprocessor controller to modulate humidifier output and maintain the highest desired space humidity possible, at all airflow volumes, without saturation of the airstream. (For this application, it is recommended to use a sail type airflow-proving switch.)

###### Airflow proving switch, pressure type: Airflow proving switch shall be diaphragm-operated with pitot tube for field installation. Switch shall have an adjustable control point range of 0.05" to 12" wc (12.5 to 2988 Pa) Operating temperature range -40 to 180 F (-40 to 82 C). Compatible with 24, 120, and 240 VAC.

###### Airflow proving switch, sail type: Airflow proving switch shall be a sail operated electric switch for field installation. Switch makes @ 250 fpm (1.3 m/s), breaks @ 75 fpm (0.4 m/s). Maximum operating temperature for sail: 170 F (77 C). Maximum operating temperature for switch: 125 F (52 C).

#### 2.5	Humidifier Accessories

##### Pump, low-flow, high-temperature: Pump shall be suitable for pumping water up to 212 F (100 C). Maximum pump flow rate shall be 3.8gpm (228 gph) with a 12-foot head (36 kPa). Pump shall have a 1-gallon cast aluminum reservoir with a 3/8" pipe thread (DN10) outlet connection, two 1-1/4" (DN32) inlet openings, and integral float switch. Pump shall be used with 115 VAC. Pump also available with 230 VAC. Pump shall be UL recognized and wired per NEC requirements.

##### Pump, high-flow, high-temperature: Pump shall be suitable for pumping water up to 212 F (100 C). Maximum pump flow rate shall be 55 gpm (3300 gph) with a 12-foot head (36 kPa). Pump shall have a 4-gallon cast aluminum reservoir with vapor seal, a 3/4" pipe thread (DN20) outlet connection, a 1-1/2" pipe thread (DN40) inlet connection, and integral float switch. Pump shall be used with 115 VAC. Pump can be wired for use with 115/230 VAC. Pump shall be UL recognized and wired per NEC requirements.

##### Pump, high-flow, low-temperature: Pump shall be suitable for pumping water up to 150 F (65.5 C). Maximum pump flow rate shall be 55 gpm (3300 gph) with a 12-foot head (36 kPa). Pump shall have a 2-gallon cast aluminum reservoir, a 1" pipe thread (DN25) outlet connection, a 1-1/2" pipe thread (DN40) inlet connection, and integral float switch. Pump shall be used with 115 VAC. Pump can be wired for use with 115/230 VAC. Pump shall be UL recognized and wired per NEC requirements.

##### Drane-kooler: A thermostatically controlled water valve shall meter an amount of cold water into a stainless steel mixing chamber to temper 212 F (100 C) water with a 6 gpm (0.38 l/s) in-flow rate to a 140 F (60 C) discharge temperature to sanitary system.

#### 2.6 	Humidifier Dispersion Options

##### Ultra-sorb® steam dispersion panel:

###### The factory-assembled steam dispersion panel shall include the following components:

Steam supply header/separator

Condensate collection header

Closely-spaced stainless steel steam dispersion tubes spanning the distance between the two headers

###### Each dispersion tube shall be fitted with two rows of steam discharge tubelets inserted into the tube wall, centered on the diametric line, and spaced 1-1/2" (38 mm) apart. Each tubelet shall be made of a thermal-resin material designed for high steam temperatures. The two rows of tubelets in each dispersion tube shall discharge steam in diametrically opposite directions, perpendicular to airflow.

###### Each tubelet shall extend through the wall of and into the center of the dispersion tube and contain a steam orifice sized for its required steam capacity.

###### The humidifier shall provide absorption characteristics that preclude water accumulation on any in-duct surface within _____" (_____ mm) of the humidifier tube panel while maintaining conditions of _____% maximum relative humidity at a minimum of _____F (_____C) in the duct airstream.

###### Air pressure loss across the humidifier panel shall not exceed _____" water column (_____ Pa) at a duct air velocity of _____fpm (_____m/s).

###### Each packaged humidifier panel assembly of tubes and headers shall be contained within a galvanized metal casing to allow convenient duct mounting, or to facilitate the end-to-end mounting of multiple humidifier panels in ducts or air handler casings. When so designated, the humidifier panel shall be shipped unassembled.

###### All tubes and headers shall be 304 stainless steel and be Heli-arc welded.

###### Tubes shall be joined to headers with slip-fit couplings.

###### Option: Tubes shall be joined to headers with EPDM hose cuffs with nylon clamps.

###### Option: Casing assembly shall be 304 stainless steel.

###### Option: Tubes and headers shall be 316 stainless steel and be Heli-arc welded.

###### Option: High-efficiency dispersion tubes

Dispersion tubes shall be insulated with a plenum-approved insulating material for in-duct installation and have an R-value not less than 0.5 at a thickness not more than 0.125" (3.2 mm), for minimal increase in dispersion tube diameter.

Airstream heat gain shall not exceed the values as scheduled; the values shall be supported by the manufacturer's published data.

Insulating material shall meet the following criteria at 0.125" (3.2 mm) thickness:

Fire/smoke index shall be 0/0 per any of the following test procedures:
-  UL 723 fire/smoke index (Test for Surface Burning Characteristics of Building Materials) 
-  NFPA 255 (Standard Method of Test of Surface Burning Characteristics of Building
    Materials)
-  ASTM E84 (Surface Burning Characteristics for Materials Used in Plenums)

Stable up to 300 °F (148 °C) continuous — to prevent material degradation, hardening, or crumbling at high temperatures

Closed-cell construction does not absorb water or support microbial growth — to negate the need for vapor barriers and jackets

Non-toxic and pure as documented in manufacturer's data — to prevent off-gassing and to facilitate use in clean rooms, pharmaceutical applications, and food industries

Will not degrade when exposed to UVC light — to negate the need for UV wraps

Continuous, seam-welded, and held in place without bands or clamps — to minimize surfaces for the accumulation of particulate matter

##### Rapid-sorb® dispersion panel:

###### Each tube bank shall consist of a horizontal header/separator and designated quantity of stainless steel vertical dispersion tubes necessary to achieve the required steam capacity and absorption distance.

###### The humidifier shall provide absorption characteristics that preclude water accumulation on any in-duct surface within _____" (_____ mm) of the humidifier tube panel while maintaining conditions of _____% maximum relative humidity at a minimum of _____F (_____C) in the duct airstream.

###### Air pressure loss across the humidifier panel shall not exceed _____" water column (_____ Pa) at a duct air velocity of _____fpm (_____m/s).

###### Header/separator shall span the width of the duct, be constructed of stainless steel and be fitted with connections for dispersion tubes.

The dispersion tubes shall extend the height of the duct and shall be fitted with two rows of tubelets on the diametric centerline and spaced 1-1/2" (38 mm) apart.

Each tubelet shall be made of a thermal-resin material designed for high steam temperatures.

Each tubelet shall extend through the wall of and into the center of the dispersion tube and contain a steam orifice sized for its required steam capacity.

For securing the upper ends of the tubes, a 3/4" x 2" (19 mm x 50 mm) stainless steel L-bracket and hardware shall be furnished, which the installer shall attach to the duct or housing.

###### Option: High-efficiency dispersion tubes

Dispersion tubes shall be insulated with a plenum-approved insulating material for in-duct installation and have an R-value not less than 0.5 at a thickness not more than 0.125" (3.2 mm), for minimal increase in dispersion tube diameter.

Airstream heat gain shall not exceed the values as scheduled; the values shall be supported by the manufacturer's published data.

Insulating material shall meet the following criteria at 0.125" (3.2 mm) thickness:

Fire/smoke index shall be 0/0 per any of the following test procedures:
-  UL 723 fire/smoke index (Test for Surface Burning Characteristics of Building Materials) 
-  NFPA 255 (Standard Method of Test of Surface Burning Characteristics of Building
    Materials)
-  ASTM E84 (Surface Burning Characteristics for Materials Used in Plenums)

Stable up to 300 °F (148 °C) continuous — to prevent material degradation, hardening, or crumbling at high temperatures

Closed-cell construction does not absorb water or support microbial growth — to negate the need for vapor barriers and jackets

Non-toxic and pure as documented in manufacturer's data — to prevent off-gassing and to facilitate use in clean rooms, pharmaceutical applications, and food industries

Will not degrade when exposed to UVC light — to negate the need for UV wraps

Continuous, seam-welded, and held in place without bands or clamps — to minimize surfaces for the accumulation of particulate matter

##### Single tube dispersion:

###### Dispersion tube(s) shall be fabricated of stainless steel tubing with uniformly spaced tubelets for steam dispersion. Each tubelet shall be made of a thermal-resin material designed for high steam temperatures. Each tubelet shall extend through the wall and to the center of dispersion tube and incorporate a properly sized calibrated orifice.

###### Dispersion tube(s) shall be pitched 2"/ft (15%) toward humidifier to allow condensate to return to humidifier.

##### Single tube dispersion with condensate drain:

###### Dispersion tube(s) shall be fabricated of stainless steel tubing with uniformly spaced tubelets for steam dispersion. Each tubelet shall be made of a thermal-resin material designed for high steam temperatures. Each tubelet shall extend through the wall and to the center of dispersion tube and incorporate a properly sized calibrated orifice.

###### Dispersion tube(s) shall be pitched 1/8"/ft (1%) minimum toward the condensate drain to allow condensate to leave the dispersion tube via the condensate drain tube.

###### The condensate drain tube shall be stainless steel tubing.

##### SDU-I fan (Space Distribution Unit, Internal absorption fan):

###### Mounted remotely from the humidifier shall be a fan-based space distribution unit (SDU-I) that provides total internal steam absorption. The SDU-I shall draw air from the side, humidify that air, and return it to the space from the front with no visible vapor.

###### The SDU-I shall have a welded stainless steel frame assembly housing an electric fan, fan control devices, steam inlet connection and internal dispersion device.

###### The SDU-I shall have a resin cabinet suitable for use in finished spaces.

###### The SDU-I shall be specified for humidifier models with capacity up to 30 lbs/hr (13.6 kg/h).

###### The SDU-I shall discharge fully absorbed humidified air in spaces where RH is 45% or less.

##### SDU-E fan (Space Distribution Unit, External absorption fan):

###### Mounted remotely from the humidifier shall be a fan-based space distribution unit (SDU-E) that shall draw air from the side and discharge visible steam vapor with a uniform rise, spread and throw out the front.

###### The SDU-E shall have a welded stainless steel frame assembly housing an electric fan, fan control devices, steam inlet connection and integral dispersion device.

###### The SDU-E shall have a resin cabinet suitable for use in finished spaces.

###### The SDU-E shall be specified for humidifier models with capacity up to 102 lbs/hr (46.3 kg/h).

##### Area-type™ fan:

###### The Area-type fan shall be specified for humidifier models with capacity up to 300 lbs/hr (136 kg/h) (not available for one-heater models).

###### The Area-type fan shall have a three-speed motor that operates using 120 V, 50/60 Hz electrical supply.

###### The Area-type fan shall have an 18" blade diameter, and operate at 1500 rpm and capacity of 5350 cfm (2.5 m3/s) on high speed (only available for six-heater, nine-heater or twelve-heater models).

###### The Area-type fan shall be field-mounted with supplied mounting bracket to the humidifier cover. Wiring shall be connected to terminals in the control cabinet.

### PART 3 — EXECUTION

#### 3.1	Installation

##### Install per manufacturer’s printed instructions and as indicated on drawings.

##### Coordinate electrical connections as specified in Division 26.

END OF SECTION