# SECTION 23 25 00

# DriSteem®’s Hydrotrue®: RO-400 series Reverse Osmosis System

### PART 1 — GENERAL

#### 1.1	Summary

##### Section includes:

###### DriSteem Hydrotrue® RO-400 series Reverse Osmosis System

##### Related items:

###### Electrical Service and Connections: Division 26

#### 1.2	References

##### Quality assurance:

###### Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authority having jurisdiction, and marked for intended use.

###### ISO 9001-2015 certified

###### Certifications, C-UL 508A Listed

#### 1.3	Submittals

##### Comply with Submittal Procedures and Execution and Closeout Requirements in General Requirements.

##### Submit product data (manufacturer’s specifications and technical data including performance, construction and fabrication) for each manufactured component.

#### 1.4	Warranty

##### Product shall be warranted to be free from defects in materials and fabrication for a period of two years after installation or 27 months from ship date.

### PART 2 — PRODUCTS

#### 2.1	System shall be DriSteem Hydrotrue:RO-400 series Reverse Osmosis System or engineer-approved equal and include all of the following integrated sub-systems:

Prefiltering

Reverse-osmosis unit (RO) water treatment system

System controls

Pressurized or atmospheric storage

##### Hydrotrue RO system: RO water treatment system shall include:

###### Frame: Frame shall be steel, primed and finished with powder-coat epoxy paint. Frame shall be equipped for and support loads imposed during rigging and operation. Frame shall house RO pump and system control components described below.

###### RO system sizing: RO system shall be rated for flow at 50°F inlet water temperature.

###### RO Membrane Sliding Rack: RO system shall have sliding rack(s) for easy membrane removal

###### RO components: RO water treatment system components shall be prewired and sized to full load capacity. Components, features, and functions shall include:

Multistage pump with all-stainless-steel body and acetyl wetted parts

Totally-enclosed fan-cooled (TEFC) high-efficiency motor

RO membrane(s): Extra low energy thin-film composite (TFC), high-efficiency, high-flow filtering membrane(s)

RO Pressure Vessel(s): Stainless steel with clamp style (U-pin not acceptable)

Feed water temperature transmitter

Automatic inlet feed solenoid valve, brass construction

Permeate flow meter, panel mounted

Concentrate flow meter, panel mounted, with needle valve

Recycle flow meter, panel mounted, with needle valve

Stainless steel pump throttling valve

Low pressure pump protection

Pressure transmitter tank pressure; 316L SS material {pressurized tanks only}

Liquid filled pressure gauges for filter in/out and system pressures, panel mounted, SS construction

Product TDS displayed on controller

System on-off with remote pressure kit or on-off with a level switch

Microprocessor controller with LED keypad display

Water supply solenoid valve, brass body

Water inlet low-pressure detection

5-micron prefilter element and housing

Pressure relief valve, mechanical, permeate service

Automatic membrane fast flush on startup capability

Automatic membrane flush based on inactivity capability

Permeate divert valve, SS construction, automatically actuated

Color coded plumbing for ease of troubleshooting

Pressurized RO holding tank or atmospheric storage tank with level sensor

Manufacturer shall provide the permeate manifold material as {stainless steel with stainless steel compression fittings or nylon tubing with polypropylene quick connect fittings}

##### Hydrotrue: RO permeate storage tank with the following features:

###### FRP pressurized storage tank: Manufacturer shall provide an 80 gallon FRP storage tank with rubber bladder. The tank shall have one water connection and an air Schrader valve to fill the bladder side with compressed air.

###### Carbon steel pressurized storage tank: Manufacturer shall provide an {120, 158, or 212} gallon painted carbon steel storage tank with rubber bladder. The tank shall have one water connection and an air Schrader valve to fill the bladder side with compressed air.

###### Atmospheric storage tank: Manufacturer shall provide a {165 or 300} gallon low density polyethylene storage tank. The tank shall have the following features:

The tank shall have a connection for inlet, vent/overflow, outlet/drain, level sensor, and lid.

The tank shall be mounted to a steel, primed and finished with powder-coat epoxy paint. Frame shall be equipped for and support loads imposed during rigging and operation. Frame shall house forwarding pump, tank and accessories.

The system shall include a transfer forwarding pump with the following capabilities:

Dry run protection

Over voltage and under voltage protection

Built in pressure sensor and smart control for pressure setpoint

The system shall include an ultraviolet disinfection module with a dosage rate of 30 mJ/cm2 at 3.5 GPM.

The tank shall come equipped with a float style level switch.

System shall be pre-plumbed and pre-wired to ease installation. The connection points that will need to be connected to include: inlet (RO permeate), outlet, drain, overflow, and one power drop. The plumbing shall be schedule 80 PVC.

##### Water Reclaim System:

###### Atmospheric storage tank: Manufacturer shall provide a {165 or 300} gallon low density polyethylene storage tank. The tank shall have the following features:

The tank shall have a connection for inlet, vent/overflow, outlet/drain, level sensor, and lid.

The tank shall be mounted to a steel, primed and finished with powder-coat epoxy paint. Frame shall be equipped for and support loads imposed during rigging and operation. Frame shall house forwarding pump, tank and accessories.

The system shall include a transfer forwarding pump with the following capabilities:

Dry run protection

Over voltage and under voltage protection

Built in pressure sensor and smart control for pressure setpoint

The system shall include an ultraviolet disinfection module with a dosage rate of 30 mJ/cm2 at 3.5 GPM.

The tank shall come equipped with a float style level switch.

System shall be pre-plumbed and pre-wired to ease installation. The connection points that will need to be connected to include: inlet (humidifier drain pan captured water), outlet (sent to the inlet of the RO system for reprocessing), drain, overflow, and one power drop. The plumbing shall be schedule 80 PVC.

The system shall include a microprocessor controller that receives the level switch and activates the use of 2 solenoid valves provided. This controller will utilize the reclaim water when present instead of fresh makeup water to supply the RO station.

The two solenoid valves will be made of {insert material} and be actuated with 24 VAC from the controller. These valves will be supplied loose for field installation.

Condensate pumps shall be supplied loose according to the schedule. The features of each pump shall include:

Dual voltage motor, 1/2HP, 230V/115V, single phase

Performance of 40 gpm @36’ TDH

Dimensions of 12” L x 12” W x 19” H

Inlet size of 1.5” NPT, female

Outlet size of 1” NPT, female

##### Vapor-logic® microprocessor controller with the following features or functions:

###### Web interface and server, included standard on all models:

Web interface shall have same functionality as Vapor-logic keypad/display

Web interface shall allow multiple remotely located users to simultaneously view system operation and/or change system parameters.

Web interface shall have password-protected secure access.

Web interface shall be compatible with standard Internet browsers.

Web interface shall connect directly to a personal computer or through a system network via Ethernet cable.

Automatic cable configuration shall allow straight-through or crossover cables.

###### Interoperable with any BACnet®, Lontalk®, and Modbus® network

###### USB port on the control board for software updates, data backups, and data restoration

###### Up-time optimizer function to keep ROs operating through conditions such as fill, drain, or run-time faults, as long as safety conditions are met, minimizing production down-time

###### Real-time clock to allow time-stamped alarm/message tracking, and scheduled events

###### Factory commissioning of control board, including system configuration as-ordered

###### Keypad/display operable within a temperature range of 32 to 158 (F (0 to 70 (C), and that provides backlighting for viewing in low light

###### Alarms, unit configuration, and usage timer values shall remain in nonvolatile memory indefinitely during a power outage.

###### The capability to monitor, control, and/or adjust the following parameters:

System alarms and system messages, current and previous

Adjustable water flush duration and frequency

Programmable outputs for remote signaling of alarms and/or messages

System diagnostics that include:

Test outputs function to verify component operation

Test RO function, by simulating demand to validate performance

Data collection of TDS, water pump hours, alarms, and service messages for viewing from the keypad/display or Web interface

Password-protected system parameters

Keypad/display or Web interface displays in English languages

Numerical units displayed in inch-pound or SI units

### PART 3 — EXECUTION

#### 3.1	Installation

##### Install per manufacturer's printed instructions and as indicated on drawings.

##### Coordinate electrical connections as specified in Division 26.

#### 3.2	Commissioning

##### The complete system, as described above, shall be fully commissioned by factory-trained technicians. Commissioning of the system shall be coordinated with commissioning of the building automation system.

# END OF SECTION