## Sheet1
Model | Phase | Volts | Standard Cylinder Kit 350-1250 uS/cm | Low Conductivity Cylinder Kit 125-350 uS/cm | Nominal current reached
XTP002 | 1 | 120 | 194601-001 | 194601-080
|  | 208 | 194601-001 | 194601-080
|  | 230 | 194601-101 | 194601-180
|  | 240 | 194601-001 | 194601-080
XTP003 | 1 | 208 | 194601-001 | 194601-080
|  | 230 | 194601-101 | 194601-180
|  | 240 | 194601-001 | 194601-080
|  | 277 | 194601-001 | 194601-080
|  | 400 | 194601-102 | 194601-101 | 1 hour 13 min
|  | 480 | 194601-002 | N/A
|  | 600 | 194601-003 | 194601-002
| 3 | 208 | 194601-004 | N/A
|  | 240 | 194601-004 | N/A
|  | 400 | 194601-105 | N/A | 35 min at 125 uS | 194600-104
|  | 480 | 194601-006 | 194601-005
|  | 600 | 194601-007 | 194601-006
XTP006 | 1 | 208 | 194601-008 | N/A
|  | 230 | 194601-108 | N/A
|  | 240 | 194601-008 | N/A
|  | 277 | 194601-008 | N/A
|  | 400 | 194601-109 | 194601-108
|  | 480 | 194601-010 | 194601-008 | 1 hour 55 min at 125 | 4 hour at 65 uS
|  | 600 | 194601-011 | 194601-009
| 3 | 208 | 194601-011 | N/A
|  | 240 | 194601-011 | N/A
|  | 400 | 194601-112 | 194601-111
|  | 480 | 194601-013 | 194601-012
|  | 600 | 194601-014 | 194601-013
XTP010 | 3 | 208 | 194601-015 | N/A
|  | 240 | 194601-015 | N/A
|  | 400 | 194601-016 | N/A
|  | 480 | 194601-017 | 194601-016
|  | 600 | 194601-018 | 194601-017
XTP017 | 3 | 208 | 194601-019 | 194601-015
|  | 240 | 194601-019 | 194601-015
|  | 400 | 194601-020 | 194601-019
|  | 480 | 194601-022 | 194601-020
|  | 600 | 194601-022 | 194601-020
XTP025 | 3 | 400 | 194601-023 | 194601-030
|  | 480 | 194601-025 | 194601-023
|  | 600 | 194601-025 | 194601-023
XTP033 | 3 | 400 | 194601-026 | 194601-027
|  | 480 | 194601-028 | 194601-026 | 1 hour 35 min
|  | 600 | 194601-028 | 194601-031
XTP042 * | 3 | 400 | 194601-026 | 194601-027
|  | 480 | 194601-028 | 194601-026
|  | 600 | 194601-028 | 194601-031 | 26 min for 125 u/S | 194600-031
XTP048 * | 3 | 400 | 194601-026 | 194601-027
|  | 480 | 194601-028 | 194601-026
|  | 600 | 194601-028 | 194601-031 | 26 min for 125 u/S | 194600-031
XTP050 ** | 3 | 400 | 194601-023 | 194601-030
|  | 480 | 194601-025 | 194601-023
|  | 600 | 194601-025 | 194601-023
XTP067 ** | 3 | 400 | 194601-026 | 194601-027
|  | 480 | 194601-028 | 194601-026
|  | 600 | 194601-028 | 194601-031
XTP083 ** | 3 | 400 | 194601-026 | 194601-027
|  | 480 | 194601-028 | 194601-026
|  | 600 | 194601-028 | 194601-031 | 26 min for 125 u/S | 194600-031
XTP096 ** | 3 | 400 | 194601-026 | 194601-027
|  | 480 | 194601-028 | 194601-026
|  | 600 | 194601-028 | 194601-031 |  | 194600-031

## Sheet2
| Item | Description | Dia | Phase | Outlet | New Description
| 194601-080 | Low conductivity 5" cylinder kit for XTR and XTP002/003 120-277V, 1P, 1" outlet | 5" | 1 | 1" | Kit Cyl XT 5" 1Ph Out 1" #2
KIT CYL XT-5/10 XT-002/003 120-277V 1P 22MM | 194601-180 | Low conductivity 5" cylinder kit for XTR and XTP002/003 120-277V, 1P, 22/25mm outlet | 5" | 1 | 22/25mm | Kit Cyl XT 5" 1Ph 22/25mm Out #2
KIT CYL XTR XT-5/10 XT-002/003 120-277V 1P | 194601-001 | Standard 5" cylinder kit for XTR and XTP002/003 120-277V, 1P, 1" outlet. Could be used as low conductivity cylinder kit for XTP003 400V, 1P, 1" outlet | 5" | 1 | 1" | Kit Cyl XT 5" 1Ph Out 1" #4
KIT CYL XT-5/10 XT-002/003 120-277V 1P 22MM | 194601-101 | Standard 5" cylinder kit for XTP002/003 230V, 1P, 22/25mm outlet. | 5" | 1 | 22/25mm | Kit Cyl XT 5" 1Ph 22/25mm Out #4
KIT CYL XT-10 XT-003 400/480V 1P | 194601-002 | Standard 5" cylinder kit for XTP003 400/480V, 1P, 1" outlet. Could be used as low conductivity cylinder kit for XTP003 600V, 1P, 1" outlet. | 5" | 1 | 1" | Kit Cyl XT 5" 1Ph Out 1" #6
KIT CYL XT-10 XT-003 400/480V 1P 22MM | 194601-102 | Standard 5" cylinder kit for XTP003 400/480V, 1P, 1" outlet. Could be used as low conductivity cylinder kit for XTP003 600V, 1P, 22/25mm outlet. | 5" | 1 | 22/25mm | Kit Cyl XT 5" 1Ph 22/25mm Out #6
KIT CYL XT-10 XT-003 600V 1P | 194601-003 | Standard 5" cylinder kit for XTP003 600V, 1P, 1" outlet. | 5" | 1 | 1" | Kit Cyl XT 5" 1Ph Out 1" #8
KIT CYL XT-10 XT-003 208/240V 3P | 194601-004 | Standard 5" cylinder kit for XTP003 208/240V, 3P, 1" outlet. | 5" | 3 | 1" | Kit Cyl XT 5" 3Ph Out 1" #2
KIT CYL XT-10 XT-003 208/240V 3P 22MM | 194601-104 | Standard 5" cylinder kit for XTP003 208/240V, 3P, 22/25mm outlet. | 5" | 3 | 22/25mm | Kit Cyl XT 5" 3Ph 22/25mm Out #2
KIT CYL XT-10 XT-003 380/400V 3P | 194601-005 | Low conductivity 5" cylinder kit for XTP003 480V, 3P, 1" outlet | 5" | 3 | 1" | Kit Cyl XT 5" 3Ph Out 1" #4
KIT CYL XT-10 XT-003 400V 3P 22MM | 194601-105 | Standard 5" cylinder kit for XTP003 400V, 3P, 22/25 mm outlet. | 5" | 3 | 22/25mm | Kit Cyl XT 5" 3Ph 22/25mm Out #4
KIT CYL XT-10 XT-003 480V 3P | 194601-006 | Standard 5" cylinder kit for XTP003 480V, 3P, 1" outlet. Could be used as low conductivity cylinder kit for XTP003 600V, 3P, 1" outlet. | 5" | 3 | 1" | Kit Cyl XT 5" 3Ph Out 1" #6
KIT CYL XT-10 XT-003 600V 3P | 194601-007 | Standard 5" cylinder kit for XTP003 600V, 3P, 1" outlet. | 5" | 3 | 1" | Kit Cyl XT 5" 3Ph Out 1" #8
KIT CYL XT-10 XT-003 600V 3P 22MM | 194601-107 |  | 5" | 3 | 22/25mm | Kit Cyl XT 5" 3Ph 22/25mm Out #8
KIT CYL XT-20 XT-006 208-277V 1P | 194601-008 | Standard 7" cylinder kit for XTP006 208-277V, 1P, 1" outlet. Could be used as low conductivity cylinder kit for XTP006 480V, 1P, 1" outlet. | 7" | 1 | 1" | Kit Cyl XT 7" 1Ph Out 1" #4
KIT CYL XT-20 XT-006 208/277V 1P 22MM | 194601-108 | Standard 7" cylinder kit for XTP006 208-277V, 1P, 22/25mm outlet. Could be used as low conductivity cylinder kit for XTP006 400V, 1P, 22/25mm outlet. | 7" | 1 | 22/25mm | Kit Cyl XT 7" 1Ph 22/25mm Out #4
KIT CYL XT-20 XT-006 400/480V 1P | 194601-009 | Standard 7" cylinder kit for XTP006 400/480V, 1P, 1" outlet. Could be used as low conductivity cylinder kit for XTP006 600V, 1P, 1" outlet. | 7" | 1 | 1" | Kit Cyl XT 7" 1Ph Out 1" #6
KIT CYL XT-20 XT-006 400/480 1P 22MM | 194601-109 | Standard 7" cylinder kit for XTP006 400V, 1P, 22/25 mm outlet. | 7" | 1 | 22/25mm | Kit Cyl XT 7" 1Ph 22/25mm Out #6
KIT CYL XT-20 XT-006 600V 1P | 194601-010 | Standard 7" cylinder kit for XTP006 600V, 1P, 1" outlet. | 7" | 1 | 1" | Kit Cyl XT 7" 1Ph Out 1" #8
KIT CYL XT-20 XT-006 208/240V 3P | 194601-011 | Standard 7" cylinder kit for XTP006 208/240V, 1P, 1" outlet | 7" | 3 | 1" | Kit Cyl XT 7" 3Ph Out 1" #2
KIT CYL XT-20 XT-006 208/240V 3P 22MM | 194601-111 | Low conductivity 7" cylinder kit for XTP006 208/240V, 3P, 22/25mm outlet | 7" | 3 | 22/25mm | Kit Cyl XT 7" 3Ph 22/25mm Out #2
KIT CYL XT-20 XT-006 380/400V 3P | 194601-012 | Low conductivity 7" cylinder kit for XTP006 380/400V, 3P, 1" outlet | 7" | 3 | 1" | Kit Cyl XT 7" 3Ph Out 1" #4
KIT CYL XT-20 XT-006 400V 3P 22MM | 194601-112 | Standard 7" cylinder kit for XTP006 400V, 3P, 22/25mm outlet | 7" | 3 | 22/25mm | Kit Cyl XT 7" 3Ph 22/25mm Out #4
KIT CYL XT-20 XT-006 480V 3P | 194601-013 | Standard 7" cylinder kit for XTP006 480V, 3P, 1" outlet. Could be used as low conductivity cylinder kit for XTP006 600V, 3P, 1" outlet. | 7" | 3 | 1" | Kit Cyl XT 7" 3Ph Out 1" #6
KIT CYL XT-20 XT-006 600V 3P | 194601-014 | Standard 7" cylinder kit for XTP006 600V, 3P, 1" outlet | 7" | 3 | 1" | Kit Cyl XT 7" 3Ph Out 1" #8
KIT CYL XT-20 XT-006 600V 3P 22MM | 194601-114 |  | 7" | 3 | 22/25mm | Kit Cyl XT 7" 3Ph 22/25mm Out #8
KIT CYL XT-30 XT-010 380/400V 3P | 194601-016 | Standard 10" cylinder kit for XTP010 380/400V, 3P, 35/38mm outlet. Could be used as low conductivity cylinder kit for XTP010 480V, 3P, 35/38mm outlet. | 10" | 3 | 35/38mm | Kit Cyl XT 10" 3Ph 3E 35/38mm Out #2
KIT CYL XT-30 XT-010 480V 3P | 194601-017 | Standard 10" cylinder kit for XTP010 480V, 3P, 35/38mm outlet. Could be used as low conductivity cylinder kit for XTP010 600V, 3P, 35/38mm outlet. | 10" | 3 | 35/38mm | Kit Cyl XT 10" 3Ph 3E 35/38mm Out #4
KIT CYL XT-30 XT-010 600V 3P | 194601-018 | Standard 10" cylinder kit for XTP010 600V, 3P, 35/38mm outlet | 10" | 3 | 35/38mm | Kit Cyl XT 10" 3Ph 3E 35/38mm Out #6
KIT CYL XT-50 XT-017 208/240V 3P | 194601-019 | Standard 10" cylinder kit for XTP017 208/240V, 3P, 35/38mm outlet. Could be used as low conductivity cylinder kit for XTP017 400V, 3P, 35/38mm outlet. | 10" | 3 | 35/38mm | Kit Cyl XT 10" 3Ph 6E 35/38mm Out #2
KIT CYL XT-30 XT-010 208/240V 3P | 194601-015 | Standard 10" cylinder kit for XTP010 208/240V, 3P, 35/38mm outlet. Could be used as low conductivity cylinder kit for XTP017 208/240V, 3P, 35/38mm outlet. | 10" | 3 | 35/38mm | Kit Cyl XT 10" 3Ph 6E 35/38mm Out #4
KIT CYL XT-50 XT-017 380/400V 3P | 194601-020 | Standard 10" cylinder kit for XTP017 380/400V, 3P, 35/38mm outlet. Could be used as low conductivity cylinder kit for XTP017 480/600V, 3P, 35/38mm outlet. | 10" | 3 | 35/38mm | Kit Cyl XT 10" 3Ph 6E 35/38mm Out #6
KIT CYL XT-50 XT-017 480/600V 3P | 194601-022 | Standard 10" cylinder kit for XTP017 480/600V, 3P, 35/38mm outlet | 10" | 3 | 35/38mm | Kit Cyl XT 10" 3Ph 6E 35/38mm Out #8
| 194601-030 | Low conductivity 12" cylinder kit for XTP025 400V, 3P, 35/38mm outlet | 12" | 3 | 35/38mm | Kit Cyl XT 12" 3Ph 35/38mm Out #4
KIT CYL XT-75/150 XT-025/050 380V 3P | 194601-023 | Standard 12" cylinder kit for XTP025/050 400V, 3P, 35/38mm outlet. Could be used as low conductivity cylinder kit for XTP025/050 480/600V, 3P, 35/38mm outlet | 12" | 3 | 35/38mm | Kit Cyl XT 12" 3Ph 35/38mm Out #6
KIT CYL XT-75/150 XT-025/050 400-600V 3P | 194601-025 | Standard 12" cylinder kit for XTP025/050 480/600V, 3P, 35/38mm outlet. | 12" | 3 | 35/38mm | Kit Cyl XT 12" 3Ph 35/38mm Out #8
KIT CYL XT-033-096 3P LC | 194601-027 | Low conductivity 12" cylinder kit for XTP042/048/067/083/096 400V, 3P, dual- 35/38mm outlet. | 12" | 3 | dual - 35/38mm | Kit Cyl XT 12" 3Ph Dual 35/38mm Out #2
KIT CYL XT-100/200 XT-033-096 380/400V 3P | 194601-026 | Standard 12" cylinder kit for XTP033/042/048/067/083/096 400V, 3P, dual- 35/38mm outlet. | 12" | 3 | dual - 35/38mm | Kit Cyl XT 12" 3Ph Dual 35/38mm Out #4
| 194601-031 | Low conductivity 12" cylinder kit for XTP033/067 600V, 3P, dual- 35/38mm outlet. | 12" | 3 | dual - 35/38mm | Kit Cyl XT 12" 3Ph Dual 35/38mm Out #6
KIT CYL XT-100/200 XT-033-096 480/600V 3P | 194601-028 | Standard 12" cylinder kit for XTP033/042/048/067/083/096 480/600V, 3P, dual- 35/38mm outlet. | 12" | 3 | dual - 35/38mm | Kit Cyl XT 12" 3Ph Dual 35/38mm Out #8